# Cooling station for RWR 3-A,

# KS-UK RWR 3-A shelf trolleys

Dimensions

Length:				approx. 1,290 mm

Depth:				approx. 1,110 mm

Height:				approx. 1,375 mm

###### Application

Cooling station for RWR 3 KS and RWR 3-A KS shelf trolleys, for maintaining the cold temperature of food supplied in the shelf trolley for portioning on a food distribution conveyor. The cooling station is connected to a customer-supplied refrigeration system.

###### Model

Design

The cooling station is a fixed-position floor unit and stands on six feet made of stainless steel, which can be adjusted to compensate for uneven floors.

The cooling station is permanently anchored to the floor with one fixing disk for each foot.  The fixing disks are included in the scope of delivery.

The unit body is made of torsion-resistant stainless steel. The surface is micro-polished. The cooling station consists of two side walls and one rear wall. The body is double-walled and insulated with polyurethane foam panels.

On the operator side, there are 2 double-walled, insulated doors split at a ratio of 2/3 to 1/3. The 
2/3 door can be swivelled to an opening angle of 270°, while the 1/3 door can be opened by 90°. If the refrigeration connection is located on the left, the 1/3 door is also located on the left.

The intake duct is behind the doors in the lower area. It can be folded upward for cleaning.

Additional guide rails are located on the left and right sides and simplify handling when rolling in the shelf trolley.

The intake duct and the side guide rails (roll-in aids) form a unit.

The main cooling system, including fans, air guidance and condensation-water collecting unit, is integrated in the three-part rear wall of the body, which can be accessed for maintenance and servicing. The central On/Off switch and the digital temperature controller are positioned in an easily accessible location in the centre on the operator side.

The mains connection cable with a Schuko plug and the connections for the refrigerant and the condensation water can be guided out of the unit on the the left, right or centre.

Active convection cooling

Cooling is controlled by the digital temperature controller.

The temperature can be regulated down to the degree from +4°C to +12°C (at an ambient temperature of +32°C).

The powerful convection fan circulates the cold air in the unit, and therefore also in the shelf trolley. The cold air is exhausted uniformly on all levels of the shelf trolley via the air outlet openings on the rear wall. The attachment of the RWR 3-A KS is also specifically refrigerated with a separate cold-air curtain.

The cold air glides over the shelf trolley and is then guided through the intake duct again and then through the refrigeration package in the rear wall of the body. The intake air is drawn through removable and replaceable expanded wire mesh filters. This prevents any dirt and impurities, particularly from

the kitchen floor, from being drawn into the interior of the

cooling station.

The double-walled and insulated doors on the operator side prevent cold loss and at the same time protect staff from the cold.

Accessories/options

- Refrigeration connection, condensation water drain and mains connection cable can be positioned to the left or right or in the middle.

- XJ485 data interface, for integration into an external control centre and data reporting

- Door version with retractable doors instead of hinged doors. The retractable doors can be pushed backwards at a 90° angle after opening, thus ensuring efficient working conditions

- Castors in place of adjustable feet, 6 steering castors, 2 of which have brakes, castor diameter 75 mm Enables more flexible use on the food distribution conveyor and facilitates the cleaning process. Only possible in conjunction with cooling brine as a refrigerant and quick-release couplings.

- Condensation water evaporator, electrically heated

- Refrigerant either R134a, R404A, R449A,

R513A or cooling brine (water glycol)

- Quick-release couplings: Quick-release couplings allow the refrigerant lines to be connected to the on-site refrigeration circuit quickly and easily. Only in conjunction with refrigerants (glycol, cooling brine) – not available in conjunction with classic refrigerants.

##### Technical data

Material:		Stainless steel

Insulating material:	Polyurethane (PU)

Weight:		Approx. 210 kg

Connected load:		220-240 V AC/ 50 Hz/

0.2 kW

Refrigerating capacity

to be installed:		2.4 kW (at t0 = -10°C)

Emissions:	The workplace-specific 	noise level of the unit is less than 70 dB(A)

Special features

- Active convection cooling

- Connection to a customer-supplied refrigeration system

- Protection type IP X5

Make

Manufacturer:			B.PRO

Model:				KS-UK RWR 3-A

Order NO.			389048